## MAG03D0424
|  |  |  | LED STATUS | relay status | On delay | off delay
DIP S/W setting | 1 : OFF
2: OFF
3: OFF
4: OFF
5: ON
| Couple voltage setting | PH-N | PH -PH
healthy condition | UV = 8% | RN : 120 |  | PWR (GREEN LED) : ON | ON | 4-6 sec | -
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV Healthy condition | UV = 8% | RN : 111.6 |  | PWR (GREEN LED) : ON | ON | Continuous ON
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV faulty condition with delay | UV = 8% | RN : 109.2 |  | PWR (GREEN LED) : ON | OFF in 2-4 sec | - | 2-4 SEC
| OV = 22% | YN : 120 |  | UV (RED LED) : ON
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | UV = 8% | RN : 110.4 |  | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| OV = 22% | YN : 120 |  | UV (RED LED) : ON
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | UV = 8% | RN : 115.2 |  | PWR (GREEN LED) : ON | ON
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Supply couple at 100 VAC
UV symmmetrical Healthy | UV = 22% | RN : 94.8 |  | PWR (GREEN LED) : ON | ON | Relay countinuous ON
| OV = 22% | YN : 94.8 |  | UV (RED LED) : OFF
| DELAY = 15 SEC | BN : 94.8 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV symmmetrical faulty | UV = 22% | RN : 92.4 |  | PWR (GREEN LED) : ON | OFF in 14-16 sec |  | 14-16 sec
| OV = 22% | YN : 92.4 |  | UV (RED LED) : ON
| DELAY = 15 SEC | BN : 92.4 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | UV = 22% | RN : 93.6 |  | PWR (GREEN LED) : ON | Continuous OFF |  | Continuous OFF
| OV = 22% | YN : 93.6 |  | UV (RED LED) : ON
| DELAY = 15 SEC | BN : 93.6 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | UV = 22% | RN : 98.4 |  | PWR (GREEN LED) : ON | ON | After 4-6 sec
| OV = 22% | YN : 98.4 |  | UV (RED LED) : OFF | After 4-6 sec
| DELAY = 15 SEC | BN : 98.4 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Supply OFF
DIP S/W setting | 1 : ON
2: ON
3: ON
4: ON
5: OFF
OV Healthy condition | UV = 22% | RN : 291 | RY : 504 | PWR (GREEN LED) : ON | ON | 5-7 sec | -
| OV = 6 % | YN : 291 | YB : 504 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 291 | BR : 504 | OV (RED LED) : OFF
ASY (RED LED): OFF
OV faulty condition | UV = 22% | RN : 296.5 | RY : 514 | PWR (GREEN LED) : ON | OFF in 4-6sec | - | 4-6sec
| OV = 6 % | YN : 296.5 | YB : 514 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 296.5 | BR : 514 | OV (RED LED) : ON
ASY (RED LED): OFF
OV hystersis not recovery | UV = 22% | RN : 291 | RY : 504 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| OV = 6 % | YN : 291 | YB : 504 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 291 | BR : 504 | OV (RED LED) : ON
ASY (RED LED): OFF
OV hystersis recovery | UV = 22% | RN : 286 | RY : 495 | PWR (GREEN LED) : ON | ON | 5-7 sec
| OV = 6 % | YN : 286 | YB : 495 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 286 | BR : 495 | OV (RED LED) : OFF
ASY (RED LED): OFF
Run time DIP switch change error
DIP S/W setting | 1 : ON | RN : 286 | RY : 495 | PWR : BLINKING | ON | Continuous ON
| 2: OFF | YN : 286 | YB : 495 | UV : BLINKING
| 3: ON | BN : 286 | BR : 495 | OV : BLINKING
| 4: ON |  |  | ASY : BLINKING
5: OFF
Supply OFF change voltages as follows before supply ON
Healthy condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Asymmetry healthy condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Continuous ON
| OV = 22 % | YN : 240 | YB : 364 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 179 | BR : 364 | OV (RED LED) : OFF
ASY (RED LED): OFF
Asymmetry faulty condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF IN 4-6 SEC |  | OFF IN 4-6 SEC
| OV = 22 % | YN : 240 | YB : 353 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 166 | BR : 353 | OV (RED LED) : OFF
ASY : BLINKING
Asymmetry not recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF |  | Continuous OFF
| OV = 22 % | YN : 240 | YB : 363 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 177 | BR : 363 | OV (RED LED) : OFF
ASY : BLINKING
Asymmetry recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
| OV = 22 % | YN : 240 | YB : 379 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 197 | BR : 379 | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase fail | UV = 22% | RN : 240 | RY : 415 | PWR : BLINKING | Instant OFF |  | Instant OFF
| OV = 22 % | YN : 240 | YB : 240 | UV (RED LED) : ON
| DELAY = 0 SEC | BN : 0 | BR : 240 | OV (RED LED) : OFF
ASY : BLINKING
Phase recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase reverse | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant OFF |  | Instant OFF
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (change phase angle) |  | ASY (RED LED): ON
Phase reverse recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (recover phase angle) |  | ASY (RED LED): OFF

## MAG03D0424EG
|  |  |  | LED STATUS | relay status | On delay | off delay
DIP S/W setting | 1 : OFF
2: OFF
3: OFF
4: OFF
5: ON
| Couple voltage setting | PH-N | PH -PH
healthy condition | UV = 8% | RN : 120 |  | PWR (GREEN LED) : ON | ON | Instant ON | -
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV Healthy condition | UV = 8% | RN : 111.6 |  | PWR (GREEN LED) : ON | ON | Continuous ON
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV faulty condition with delay | UV = 8% | RN : 109.2 |  | PWR (GREEN LED) : ON | OFF in 2-4 sec | - | 2-4 SEC
| OV = 22% | YN : 120 |  | UV (RED LED) : ON
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | UV = 8% | RN : 110.4 |  | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| OV = 22% | YN : 120 |  | UV (RED LED) : ON
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | UV = 8% | RN : 115.2 |  | PWR (GREEN LED) : ON | ON
| OV = 22% | YN : 120 |  | UV (RED LED) : OFF
| DELAY = 3SEC | BN : 120 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Supply couple at 100 VAC
UV symmmetrical Healthy | UV = 22% | RN : 94.8 |  | PWR (GREEN LED) : ON | ON | Relay countinuous ON
| OV = 22% | YN : 94.8 |  | UV (RED LED) : OFF
| DELAY = 15 SEC | BN : 94.8 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV symmmetrical faulty | UV = 22% | RN : 92.4 |  | PWR (GREEN LED) : ON | OFF in 14-16 sec |  | 14-16 sec
| OV = 22% | YN : 92.4 |  | UV (RED LED) : ON
| DELAY = 15 SEC | BN : 92.4 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | UV = 22% | RN : 93.6 |  | PWR (GREEN LED) : ON | Continuous OFF |  | Continuous OFF
| OV = 22% | YN : 93.6 |  | UV (RED LED) : ON
| DELAY = 15 SEC | BN : 93.6 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | UV = 22% | RN : 98.4 |  | PWR (GREEN LED) : ON | ON | Instant ON
| OV = 22% | YN : 98.4 |  | UV (RED LED) : OFF
| DELAY = 15 SEC | BN : 98.4 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Supply OFF
DIP S/W setting | 1 : ON
2: ON
3: ON
4: ON
5: OFF
OV Healthy condition | UV = 22% | RN : 291 | RY : 504 | PWR (GREEN LED) : ON | ON | 5-7 sec | -
| OV = 6 % | YN : 291 | YB : 504 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 291 | BR : 504 | OV (RED LED) : OFF
ASY (RED LED): OFF
OV faulty condition | UV = 22% | RN : 296.5 | RY : 514 | PWR (GREEN LED) : ON | OFF in 4-6sec | - | 4-6sec
| OV = 6 % | YN : 296.5 | YB : 514 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 296.5 | BR : 514 | OV (RED LED) : ON
ASY (RED LED): OFF
OV hystersis not recovery | UV = 22% | RN : 291 | RY : 504 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| OV = 6 % | YN : 291 | YB : 504 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 291 | BR : 504 | OV (RED LED) : ON
ASY (RED LED): OFF
OV hystersis recovery | UV = 22% | RN : 286 | RY : 495 | PWR (GREEN LED) : ON | ON | 5-7 sec
| OV = 6 % | YN : 286 | YB : 495 | UV (RED LED) : OFF
| DELAY = 6 SEC | BN : 286 | BR : 495 | OV (RED LED) : OFF
ASY (RED LED): OFF
Run time DIP switch change error
DIP S/W setting | 1 : ON | RN : 286 | RY : 495 | PWR : BLINKING | ON | Continuous ON
| 2: OFF | YN : 286 | YB : 495 | UV : BLINKING
| 3: ON | BN : 286 | BR : 495 | OV : BLINKING
| 4: ON |  |  | ASY : BLINKING
5: OFF
Supply OFF change voltages as follows before supply ON
Healthy condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Asymmetry healthy condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Continuous ON
| OV = 22 % | YN : 240 | YB : 361 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 176 | BR : 361 | OV (RED LED) : OFF
ASY (RED LED): OFF
Asymmetry faulty condition | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF IN 4-6 SEC |  | OFF IN 4-6 SEC
| OV = 22 % | YN : 240 | YB : 353 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 166 | BR : 353 | OV (RED LED) : OFF
ASY : BLINKING
Asymmetry not recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF |  | Continuous OFF
| OV = 22 % | YN : 240 | YB : 363 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 177 | BR : 363 | OV (RED LED) : OFF
ASY : BLINKING
Asymmetry recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
| OV = 22 % | YN : 240 | YB : 379 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 197 | BR : 379 | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase fail | UV = 22% | RN : 240 | RY : 415 | PWR : BLINKING | Instant OFF |  | Instant OFF
| OV = 22 % | YN : 240 | YB : 240 | UV (RED LED) : ON
| DELAY = 0 SEC | BN : 0 | BR : 240 | OV (RED LED) : OFF
ASY : BLINKING
Phase recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase reverse | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant OFF |  | Instant OFF
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (change phase angle) |  | ASY (RED LED): ON
Phase reverse recovery | UV = 22% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| OV = 22 % | YN : 240 | YB : 415 | UV (RED LED) : OFF
| DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (recover phase angle) |  | ASY (RED LED): OFF

## MAG03D0425
[6 empty] | LED STATUS | relay status | On delay | off delay
|  | DIP S/W setting | 1 : OFF
2: OFF
3: OFF
4: OFF
5: ON
|  |  | Couple voltage setting | PH-N | PH -PH
|  | healthy condition | P1 = 7% | RN : 240 |  | PWR (GREEN LED) : ON | ON | 4-6 sec | -
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 3 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV Healthy condition | P1 = 7% | RN : 226 |  | PWR (GREEN LED) : ON | ON | Continuous ON
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 3 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV faulty condition with delay | P1 = 7% | RN : 220.8 |  | PWR (GREEN LED) : ON | OFF in 2-4 sec | - | 2-4 SEC
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : ON
|  |  | DELAY = 3 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV hystersis not recovery | P1 = 7% | RN : 223.2 |  | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : ON
|  |  | DELAY = 3 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV hystersis recovery | P1 = 7% | RN : 230.4 |  | PWR (GREEN LED) : ON | ON | 4-6 sec
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 3 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Supply couple at 240 VAC
|  | OV symmmetrical Healthy | P1 = 7% | RN : 261.6 |  | PWR (GREEN LED) : ON | ON | Relay countinuous ON
|  |  | P2 = 5% | YN : 261.6 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 261.6 |  | OV (RED LED) : OFF
|  |  |  | Changed 261.6 - 261 |  | ASY (RED LED): OFF
|  | OV symmmetrical faulty | P1 = 7% | RN : 266.4 |  | PWR (GREEN LED) : ON | OFF in 14-16 sec |  | 14-16 sec
|  |  | P2 = 5% | YN : 266.4 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 266.4 |  | OV (RED LED) : ON
ASY (RED LED): OFF
|  | OV hystersis not recovery | P1 = 7% | RN : 261.6 |  | PWR (GREEN LED) : ON | Continuous OFF |  | Continuous OFF
|  |  | P2 = 5% | YN : 261.6 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 261.6 |  | OV (RED LED) : ON
ASY (RED LED): OFF
|  | OV hystersis recovery | P1 = 7% | RN : 256.8 |  | PWR (GREEN LED) : ON | ON | After 4-6 sec
|  |  | P2 = 5% | YN : 256.8 |  | UV (RED LED) : OFF | After 4-6 sec
|  |  | DELAY = 15 SEC | BN : 256.8 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | Phase fail | P1 = 7% | RN : 240 |  | PWR : BLINKING | Instant OFF |  | Instant OFF
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : ON
|  |  | DELAY = 15 SEC | BN : 0 |  | OV (RED LED) : OFF
ASY : BLINKING
After 4-6 sec
|  | Phase recovery | P1 = 7% | RN : 240 |  | PWR (GREEN LED) : ON | Instant ON | Instant ON
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Instant OFF
|  | Phase reverse (No any change) | P1 = 7% | RN : 240 |  | PWR (GREEN LED) : ON | Continuous ON | Continuous ON
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
|  |  |  | (change phase angle) |  | ASY (RED LED): OFF
After 4-6 sec
|  | Phase reverse recovery | P1 = 7% | RN : 240 |  | PWR (GREEN LED) : ON | Continuous ON | Continuous ON
|  |  | P2 = 5% | YN : 240 |  | UV (RED LED) : OFF
|  |  | DELAY = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
|  |  |  | (recover phase angle) |  | ASY (RED LED): OFF
Supply OFF
|  | DIP S/W setting | 1 : OFF
2: ON
3: ON
4: ON
5: OFF
Replace = 290
| 510.45 | OV Healthy condition | P1 = 23% | RN : 292.5 | RY : 506 | PWR (GREEN LED) : ON | ON IN 8-10SEC | 8-10 sec | -
|  |  | P2 = 25% | YN : 292.5 | YB : 506 | UV (RED LED) : OFF
|  |  | DELAY = 9 SEC | BN : 292.5 | BR : 506 | OV (RED LED) : OFF
| -4.15 |  |  |  |  | ASY (RED LED): OFF
V : 299V to go into fault
240+23% |  | OV faulty condition | P1 = 23% | RN : 297 | RY : 514.4 | PWR (GREEN LED) : ON | OFF in 4-6sec | - | 4-6sec
|  |  | P2 = 25% | YN : 297 | YB : 514.4 | UV (RED LED) : OFF
|  |  | DELAY = 9 SEC | BN : 297 | BR : 514.4 | OV (RED LED) : ON
ASY (RED LED): OFF
Fault recover at 271
|  | OV hystersis not recovery | P1 = 23% | RN : 271 | RY : 469 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
|  |  | P2 = 25% | YN : 271 | YB : 469 | UV (RED LED) : OFF
|  |  | DELAY = 9 SEC | BN : 271 | BR : 469 | OV (RED LED) : ON
ASY (RED LED): OFF
|  | OV hystersis recovery | P1 = 23% | RN : 263 | RY : 455 | PWR (GREEN LED) : ON | ON IN 8-10SEC | 8-10 sec
|  |  | P2 = 25% | YN : 263 | YB : 455 | UV (RED LED) : OFF
|  |  | DELAY = 9 SEC | BN : 263 | BR : 455 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV Healthy condition | P1 = 23% | RN : 147 | RY : 255 | PWR (GREEN LED) : ON | Continuous ON | Continuous ON
|  |  | P2 = 25% | YN : 147 | YB : 255 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 147 | BR : 255 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV faulty condition | P1 = 23% | RN : 141.5 | RY : 245 | PWR (GREEN LED) : ON | OFF in 4.6 sec | - | OFF in 4.6 sec
|  |  | P2 = 25% | YN : 141.5 | YB : 245 | UV (RED LED) : ON
|  |  | DELAY = 0 SEC | BN : 141.5 | BR : 245 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV hystersis not recovery | P1 = 23% | RN : 147 | RY : 255 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
|  |  | P2 = 25% | YN : 147 | YB : 255 | UV (RED LED) : ON
|  |  | DELAY = 0 SEC | BN : 147 | BR : 255 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | UV hystersis recovery | P1 = 23% | RN : 150 | RY : 260 | PWR (GREEN LED) : ON | Instant ON | Instant ON
|  |  | P2 = 25% | YN : 150 | YB : 260 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 150 | BR : 260 | OV (RED LED) : OFF
Run time DIP switch change error
|  | DIP S/W setting | 1 : OFF | RN : 150 | RY : 260 | PWR : BLINKING | ON | Continuous ON
|  |  | 2: OFF | YN : 150 | YB : 260 | UV : BLINKING
|  |  | 3: ON | BN : 150 | BR : 260 | OV : BLINKING
|  |  | 4: ON |  |  | ASY : BLINKING
5: OFF
|  | DIP S/W setting | 1 : OFF | RN : 150 | RY : 260 | PWR (GREEN LED) : ON | ON | Continuous ON
|  |  | 2: ON | YN : 150 | YB : 260 | UV (RED LED) : OFF
|  |  | 3: ON | BN : 150 | BR : 260 | OV (RED LED) : OFF
|  |  | 4: ON |  |  | ASY (RED LED): OFF
5: OFF
Supply OFF change voltages as follows before supply ON
|  | Asymmetry healthy condition | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
|  |  | P1 = 23% | YN : 240 | YB : 361 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 176 | BR : 361 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | Asymmetry faulty condition | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF IN 4-6 SEC |  | OFF IN 4-6 SEC
|  |  | P2 = 25% | YN : 240 | YB : 353 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 166 | BR : 353 | OV (RED LED) : OFF
ASY : BLINKING
|  | Asymmetry not recovery | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF |  | Continuous OFF
|  |  | P2 = 25% | YN : 240 | YB : 363 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 177 | BR : 363 | OV (RED LED) : OFF
ASY : BLINKING
|  | Asymmetry recovery | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON | Instant ON
|  |  | P2 = 25% | YN : 240 | YB : 379 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 197 | BR : 379 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | Phase fail | P1 = 23% | RN : 240 | RY : 415 | PWR : BLINKING | Instant OFF |  | Instant OFF
|  |  | P2 = 25% | YN : 240 | YB : 240 | UV (RED LED) : ON
|  |  | DELAY = 0 SEC | BN : 0 | BR : 240 | OV (RED LED) : OFF
ASY : BLINKING
|  | Phase recovery | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
|  |  | P2 = 25% | YN : 240 | YB : 415 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
|  | Phase reverse | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant OFF |  | Instant OFF
|  |  | P2 = 25% | YN : 240 | YB : 415 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  |  |  | (change phase angle) |  | ASY (RED LED): ON
|  | Phase reverse recovery | P1 = 23% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
|  |  | P2 = 25% | YN : 240 | YB : 415 | UV (RED LED) : OFF
|  |  | DELAY = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  |  |  | (recover phase angle) |  | ASY (RED LED): OFF

## MAG03D0426
Test cases/ parameters | POT Setting | Voltage Setting |  | LED STATUS | relay status | On delay | off delay
DIP S/W setting | 1 : OFF
2: OFF
3: OFF
4: OFF
5: ON
| Couple voltage setting | PH-N | PH -PH
healthy condition | P1 = 7 % | RN :0 |  | PWR (GREEN LED) : ON | ON | Instant ON | -
| P2 = 0 SEC | YN : 0 |  | UV (RED LED) : OFF
| P3 = 15 SEC | BN : 0 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV Healthy condition | P1 = 7 % | RN : 225.6 |  | PWR (GREEN LED) : ON | ON | Continuous ON
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : OFF
| P3 = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV faulty condition with delay | P1 = 7 % | RN : 220.8 |  | PWR (GREEN LED) : ON | OFF in 14-16 sec | - | OFF in 14-16 sec
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : ON
| P3 = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | P1 = 7 % | RN : 225.6 |  | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : ON
| P3 = 15 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | P1 = 7 % | RN : 232.1 |  | PWR (GREEN LED) : ON | ON | Instant ON
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase fail | P1 = 7 % | RN : 240 |  | PWR : BLINKING | Instant OFF |  | Instant OFF
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : ON
| P3 = 0 SEC | BN : 0 |  | OV (RED LED) : OFF
ASY : BLINKING
Phase recovery | P1 = 7 % | RN : 240 |  | PWR (GREEN LED) : ON | Instant ON | Instant ON
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 |  | OV (RED LED) : OFF
ASY (RED LED): OFF
Instant OFF
Phase reverse | P1 = 7 % | RN : 240 |  | PWR (GREEN LED) : ON | Continuous ON | Continuous ON
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 |  | OV (RED LED) : OFF
|  | (change phase angle) |  | ASY (RED LED): OFF
Phase reverse recovery | P1 = 7 % | RN : 240 |  | PWR (GREEN LED) : ON | Continuous ON | Continuous ON
| P2 = 0 SEC | YN : 240 |  | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 |  | OV (RED LED) : OFF
|  | (recover phase angle) |  | ASY (RED LED): OFF
Supply OFF
DIP S/W setting | 1 : ON
2: ON
3: ON
4: ON
5: OFF
Phase Asymmetry Healthy | P1 = 25% | RN : 89 | RY : 294 | PWR (GREEN LED) : ON | ON in 29-31 sec | ON in 29-31 sec
| P2 = 0 MIN | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 1.5 MIN | BN : 240 | BR : 294 | OV (RED LED) : OFF
ASY (RED LED): OFF
Continuous ON
Phase Asymmetry faulty | P1 = 25% | RN : 78 | RY : 287 | PWR (GREEN LED) : ON | OFF in 89-91 SEC |  | OFF in 89-91 SEC
| P2 = 0 MIN | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 1.5 MIN | BN : 240 | BR : 287 | OV (RED LED) : OFF
ASY (RED LED): BLINKING
Phase Asymmetry not recovery | P1 = 25% | RN : 95 | RY : 299 | PWR (GREEN LED) : ON | Continuous OFF |  | Continuous OFF
| P2 = 0 MIN | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 1.5 MIN | BN : 240 | BR : 299 | OV (RED LED) : OFF
ASY (RED LED): BLINKING
Phase Asymmetry recovery | P1 = 25% | RN : 105 | RY : 306 | PWR (GREEN LED) : ON | ON in 29-31 sec | ON in 29-31 sec
| P2 = 0 MIN | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 1.5 MIN | BN : 240 | BR : 306 | OV (RED LED) : OFF
ASY (RED LED): ON
| Couple all voltage |  |  | LED stays green but relay OFF | OFF
UV Healthy condition | P1 = 25% | RN : 194.1 | RY : 336 | PWR (GREEN LED) : ON | ON in 89-91 SEC | ON in 89-91 SEC | -
| P2 = 1.5 MIN | YN : 194.1 | YB : 336 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 194.1 | BR : 336 | OV (RED LED) : OFF
ASY (RED LED): OFF
UV faulty condition | P1 = 25% | RN : 189.3 | RY : 328 | PWR (GREEN LED) : ON | Instant OFF | - | Instant OFF
| P2 = 1.5 MIN | YN : 189.3 | YB : 328 | UV (RED LED) : ON
| P3 = 0 MIN | BN : 189.3 | BR : 328 | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis not recovery | P1 = 25% | RN : 194.1 | RY : 336 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| P2 = 1.5 MIN | YN : 194.1 | YB : 336 | UV (RED LED) : ON
| P3 = 0 MIN | BN : 194.1 | BR : 336 | OV (RED LED) : OFF
ASY (RED LED): OFF
UV hystersis recovery | P1 = 25% | RN : 200.5 | RY : 347 | PWR (GREEN LED) : ON | ON in 89-91 SEC | ON in 89-91 SEC
| P2 = 1.5 MIN | YN : 200.5 | YB : 347 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 200.5 | BR : 347 | OV (RED LED) : OFF
ASY (RED LED): OFF
Healthy condition | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | continuous ON |  | -
| P2 = 0 MIN | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Decouple all voltages
OV Healthy condition | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | continuous ON |  | -
| P2 = 0 MIN | YN : 240 | YB : 452 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 282 | BR : 452 | OV (RED LED) : OFF
|  | Replaced BN : 281 |  | ASY (RED LED): OFF
OV faulty condition | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant OFF | - | Instant OFF
| P2 = 0 MIN | YN : 240 | YB : 461 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 291 | BR : 461 | OV (RED LED) : ON
ASY (RED LED): OFF
OV hystersis not recovery | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | OFF | - | Continuous OFF
| P2 = 0 MIN | YN : 240 | YB : 452 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 282 | BR : 452 | OV (RED LED) : ON
ASY (RED LED): OFF
ON in 29-31 sec
OV hystersis recovery | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | ON in 89-91 SEC | ON in 89-91 SEC
| P2 = 0 MIN | YN : 240 | YB : 441 | UV (RED LED) : OFF
| P3 = 0 MIN | BN : 270 | BR : 441 | OV (RED LED) : OFF
ASY (RED LED): OFF
Run time DIP switch change error
DIP S/W setting | 1 : ON | RN : 240 | RY : 415 | PWR : BLINKING | ON | Continuous ON
| 2: ON | YN : 240 | YB : 441 | UV : BLINKING
| 3: OFF | BN : 270 | BR : 441 | OV : BLINKING
| 4: ON |  |  | ASY : BLINKING
5: OFF
Supply OFF & supply ON
Phase fail | P1 = 25% | RN : 240 | RY : 415 | PWR : BLINKING | Instant OFF |  | Instant OFF
| P2 = 0 SEC | YN : 240 | YB : 240 | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 0 | BR : 240 | OV (RED LED) : OFF
ASY : BLINKING
Phase recovery | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| P2 = 0 SEC | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
ASY (RED LED): OFF
Phase reverse | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant OFF |  | Instant OFF
| P2 = 0 SEC | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (change phase angle) |  | ASY (RED LED): ON
Phase reverse recovery | P1 = 25% | RN : 240 | RY : 415 | PWR (GREEN LED) : ON | Instant ON | Instant ON
| P2 = 0 SEC | YN : 240 | YB : 415 | UV (RED LED) : OFF
| P3 = 0 SEC | BN : 240 | BR : 415 | OV (RED LED) : OFF
|  | (recover phase angle) |  | ASY (RED LED): OFF

## MAG03D0428
|  |  | LED STATUS | relay status | On delay | off delay
| PH-N | PH -PH
healthy condition | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON | -
| YN : 240 | YB : 415
| BN : 240 | BR : 415
Phase fail | RN : 240 | RY : 415 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 240 | YB : 240
| BN : 0 | BR : 240
Phase recovery | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON
| YN : 240 | YB : 415
| BN : 240 | BR : 415
Phase reverse | RN : 240 | RY : 415 | R(RED LED) : BLINKING | Instant OFF |  | Instant OFF
| YN : 240 | YB : 415
| BN : 240 | BR : 415
(change phase angle)
Phase reverse recovery | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON
| YN : 240 | YB : 415
| BN : 240 | BR : 415
(recover phase angle)
Couple all Voltages
Lower Cut OFF healthy | RN : 107 | RY : 185 | R (RED LED) : ON | ON | Continuous ON
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF | RN : 95 | RY : 165 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 95 | YB : 165
| BN : 95 | BR : 165
Lower Cut OFF not recovery | RN : 107 | RY : 185 | R (RED LED) : OFF | OFF |  | Continuous OFF
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF recovery | RN : 120 | RY : 207 | R (RED LED) : ON | ON | Instant ON
| YN : 120 | YB : 207
| BN : 120 | BR : 207
Lower Cut OFF healthy | RN : 107 | RY : 185 | R (RED LED) : ON | ON | Continuous ON
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF | RN : 95 | RY : 165 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 95 | YB : 165
| BN : 95 | BR : 165
Lower Cut OFF not recovery | RN : 107 | RY : 185 | R (RED LED) : OFF | OFF |  | Continuous OFF
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF recovery | RN : 120 | RY : 207 | R (RED LED) : ON | ON | Instant ON
| YN : 120 | YB : 207
| BN : 120 | BR : 207
Higher Cut OFF healthy | RN : 317 | RY : 550 | R (RED LED) : ON | ON | Continuous ON
| YN : 317 | YB : 550
| BN : 317 | BR : 550
Higher Cut OFF | RN : 340 | RY : 590 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 340 | YB : 590
| BN : 340 | BR : 590

## MAG03D0427
|  |  | LED STATUS | relay status | On delay | off delay
| PH-N | PH -PH
healthy condition | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON | -
| YN : 240 | YB : 415
| BN : 240 | BR : 415
Phase fail | RN : 240 | RY : 415 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 240 | YB : 240
| BN : 0 | BR : 240
Phase recovery | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON
| YN : 240 | YB : 415
| BN : 240 | BR : 415
Phase reverse | RN : 240 | RY : 415 | R(RED LED) : ON | ON | Contonuous ON
| YN : 240 | YB : 415
| BN : 240 | BR : 415
(change phase angle)
Phase reverse recovery | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Contonuous ON
| YN : 240 | YB : 415
| BN : 240 | BR : 415
(recover phase angle)
Asymmetry healthy condition | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Continuous ON
| YN : 240 | YB : 287
| BN : 78 | BR : 287
Asymmetry faulty condition | RN : 240 | RY : 415 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 240 | YB : 257
| BN : 32 | BR : 257
Asymmetry not recovery | RN : 240 | RY : 415 | R (RED LED) : OFF | OFF |  | Continuous OFF
| YN : 240 | YB : 288
| BN : 80 | BR : 288
Asymmetry recovery | RN : 240 | RY : 415 | R (RED LED) : ON | ON | Instant ON
| YN : 240 | YB : 310
| BN : 110 | BR : 310
Couple all Voltages
Lower Cut OFF healthy | RN : 107 | RY : 185 | R (RED LED) : ON | ON | Continuous ON
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF | RN : 95 | RY : 165 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 95 | YB : 165
| BN : 95 | BR : 165
Lower Cut OFF not recovery | RN : 107 | RY : 185 | R (RED LED) : OFF | OFF |  | Continuous OFF
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF recovery | RN : 120 | RY : 207 | R (RED LED) : ON | ON | Instant ON
| YN : 120 | YB : 207
| BN : 120 | BR : 207
Repeated Tests -
Lower Cut OFF healthy | RN : 107 | RY : 185 | R (RED LED) : ON | ON | Continuous ON
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF | RN : 95 | RY : 165 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 95 | YB : 165
| BN : 95 | BR : 165
Lower Cut OFF not recovery | RN : 107 | RY : 185 | R (RED LED) : OFF | OFF |  | Continuous OFF
| YN : 107 | YB : 185
| BN : 107 | BR : 185
Lower Cut OFF recovery | RN : 120 | RY : 207 | R (RED LED) : ON | ON | Instant ON
| YN : 120 | YB : 207
| BN : 120 | BR : 207
Higher Cut OFF healthy | RN : 317 | RY : 550 | R (RED LED) : ON | ON | Continuous ON
| YN : 317 | YB : 550
| BN : 317 | BR : 550
Higher Cut OFF | RN : 340 | RY : 590 | R (RED LED) : OFF | OFF |  | Instant OFF
| YN : 340 | YB : 590
| BN : 340 | BR : 590